## Sheet1
Intstructions for this sheet: To add additional years, Highlight Column "B" and Insert New Column
Attendance Center/Facility | Year Tested for Radon | Year Tested for Radon | Year Tested for Radon | Year Tested for Radon | Year Tested for Radon
| 2023 | 2020 | 2017 | 2016 | 2013 | 2012
Aurora Heights Elementary |  | 2020-01-20 |  | 2016-12-15 | 2013-03-28
|  | Tested entire building |  | Tested entire building | Tested entire building
|  | 0>4.0 pCi/L, 2 rooms > 2.0 pCi/L |  | 0 > 4.0 pci/L, 3 rooms > 2.0 pCi/L | 0 > 4.0 pci/L, 1 rooms > 2.0 pCi/L
|  | Monitor HVAC since some > 2.0 pCi/L |  | Monitor HVAC since some > 2.0 pCi/L | Monitor HVAC
Emerson Hough Elementary |  | 2020-01-30 |  | 2016-12-15 | 2013-04-22 | Oct Nov 2012
|  | Tested Entire Building |  | Tested Entire Building | Tested Entire Building | 0>4.0 pCi/L Rooms 135, 137, 140, 141, 142, 143, 144,
|  | 0 > 4.0 pCi/L, 18 Rooms > 2.0 pCi/L |  | 0>4.0 pCi/L, 20 Rooms > 2.0 pCi/L | 0>4.0 pCi/L, 1 Room >2.0 pCi/L
|  | Consider Fixing Rooms > 2.0 pCi/L |  | Consider Fixing Rooms > 2.0 pCi/L | No action recommended | Oct Nov 2012
145, Multi Purpose and Media
Thomas Jefferson Elementary |  | 2020-02-13 | 2017-01-12 |  | 2013-03-25
|  | Tested entire building | Tested entire building |  | Tested entire building
|  | 0 > 4.0 pCi/L, 1 > 2.0 pCi/L | 0 > 4.0 pci/L, 0 rooms > 2.0 pCi/L |  | 0 > 4.0 pci/L, 0 rooms > 2.0 pCi/L
|  | No action recommended | No action recommended |  | No action recommended
Woodrow Wilson Elementary |  | 2020-02-13 | 2017-01-12 |  | 2013-03-28
|  | Tested entire building | Tested entire building |  | Tested entire building
|  | Room 114 was 5.1, CRM tested & Avg. 2.9 | 6 > 4.0 pCi/L, 19 other rooms > 2.0 pCi/L |  | 0 > 4.0 pci/L, 6 rooms > 2.0 pCi/L
|  | 6 Rooms > 2.0 pCi/L | Mitigation Recommended |  | Consider Fixing Rooms > 2.0 pCi/L
|  | CONTINUE to MONITOR HVAC | HVAC Upgraded or Replaced
|  | Consider Fixing rooms > 2.0 pCi/L | 3/6/17-4/3/17
|  | Retest as Post-Mitigation every 2 years | Rms 113, 114, 115, 116, 117, 118 all < 4.0 pC
|  | Test entire school FALL 2023 | when tested with CRM's
Berg Middle School | 2023-03-23 | 2020-01-23 | 2017-01-20 | 2014-04-06 | 2013-03-25 | 2012-12-24
| Most rooms were > 2.0 pCi/L and 31 rooms > 4.0 pCi/L | Tested entire NEW BUILDING | Retested entire building | Follow-up with CRM | Tested entire building w/kits | Tested all rooms w/CRM's
| HVAC had been accidently turned off previous week so there was ZERO fresh air in the building when we tested. | 5 Rooms > 4.0 pCi/L, 7 > 2.0 pCi/L | Rooms 250, 141, 142, Weight Rm > 4.0 pCi/L | Room 250 average was 0.2 pCi/L | Rooms 250, 251 and 252 > 4.0 pCi/L | All rooms < 4.0 pCi/L
| 4 second level rooms were tested (10%) and 1 of those had radon of 3.5 pCi/L during the March test | Diagnostic testing w/CRM's | 2017-02-09 |  | 2013-04-03
| HVAC corrected immediately | 2020-01-30 | Diagnostic testing w/CRM |  | Rooms 250, 251 and 252 < 4.0 pCi/L
| 2023-04-13 | Band and Choir Offices and Practice Rooms | Room 250 at 3.2 pCi/L (Rm 251 at 3.0 pCi/L)
| Second test of all rooms and offices with HVAC in proper working order | tested using CRM's, A105A still high during school, but is used as storage mostly | 2017-03-30
| ZERO rooms >4.0 pCi/L, 44 rooms < 0.3 (lowest detectable w/kits), | A104A and A104F still high during school, but are not occupied significantly. Check is A104A is office? How much occupied? | Diagnostic testing w/CRM
| TWO rooms > 2.0 pCi/L SRO and A104B | HVAC for that area adjusted | Room 141 at 1.7 pCi/L; 142 at 3.7 pCi/L
| RETEST coldest months Jan/Feb 2025 | Restest in 2 years as Post-Mitigation Building | New Building planned completion 2019
Newton High School |  | 2020-02-20 | 2017-02-09 |  | 2013-04-22
|  | Tested entire building | Tested entire building |  | Tested entire building
|  | 4 Rooms > 2 pCi/L; 2 Rooms > 4.0 pCi/L | 0 Rooms > 4 pCi/L; 9 Rooms > 2.0 pCi/L |  | Custodian Control Room and LL practice
|  | One high room was a Maintence Control Room, which is only used as storage NOW. This is considered a | No action recommended |  | rooms currently used as storage > 4.0 pCi/L
|  | radon entry point and should not be occupied other than for brief times. |  |  | Recommended they not significantly occupy
|  | The other high room was Lower Gym and the other Gym test kit was normal. |  |  | those rooms.
High activity areas can be a reason a kit has a high result NOT that it increases the radon, just that it causes extra dust which affects the accuracy of the radon test kit. No retest with CRM due to high activity area
No Action Recommended
West Academy & District Offices |  | 2020-03-20 | 2017-03-02
|  | Tested entire building | Tested entire building
|  | Zero Rooms > 4.0 pCi/L, 0 Rooms > 2.0 pCi/L | 0 Rooms > 4.0 pCi/L, 0 Rooms > 2.0 pCi/L
|  | No action recommended | No action recommended
Technology, Transportation and Maintenance Buildings |  | 2020-03-20 | 2017-03-02
|  | 0 Rooms > 4.0 pCi/L, 3 rooms > 2.0 pCi/L, | Technology Office all rooms > 2.0 pCi/L
Considering Fixing Rooms > 2.0 pCi/L
Transportation Building 3 rooms
3 rooms all < 1.0 pCi/L
Maintenance Offices 2 rooms
2 rooms tested, both < 1.0 pCi/L
|  | No action recommended | No action recommended